## Sheet1
DATE / COMPANY |  |  | MMS INVESTIGATION |  |  |  | LOCATION | [6 empty] | FACILITY |  |  |  |  | INCIDENT SUMMARY | INCIDENT TYPE | [28 empty] | SPILL VOLUME / PRODUCT | [7 empty] | PRIMARY OPERATION AT TIME OF INCIDENT | [8 empty] | GENERAL CAUSE
DATE | TIME | COMPANY NAME | DISTRICT (2010) | PANEL | OCS REPORT NUMBER | MMS APPROVAL DATE | OCS REGION | DISTRICT CODE | AREA CODE | BLOCK | LEASE | WATER DEPTH (feet) | DISTANCE TO SHORE (miles) | STRUCTURE NAME | STRUCTURE TYPE | RIG NAME | RIG TYPE | PIPELINE SEGMENT NUMBER |  | NUMBER FATALITIES | NUMBER INJURY 1-3 DAYS LOST TIME | NUMBER INJURY >3 DAYS LOST TIME | NUMBER INJURY 1-3 DAYS RESTRICTED WORK / JOB TRANSFER | NUMBER INJURY >3 DAYS RESTRICTED WORK / JOB TRANSFER | NUMBER INJURIES WITH NO DAYS LOST TIME, RESTRICTED WORK, OR JOB TRANSFER | INJURIES INVOVLING EVACUATION | FIRE | EXPLOSION | LOSS WELL CONTROL UNDERGROUND | LOSS WELL CONTROL SURFACE | LOSS WELL CONTROL DIVERTER | LOSS WELL CONTROL EQUIPMENT FAILURE | MINOR COLLISION (property damage ≤$25 K) | MAJOR COLLISION (property damage >$25K) | STRUCTURAL DAMAGE REQUIRING FACILITY SHUT-IN | CRANE | OTHER LIFTING DEVICE | OTHER LIFTING DEVICE NAME | DAMAGED/DISABLED SAFETY SYSTEM | DAMAGED/DISABLED SAFETY SYSTEM NAME | REPORTABLE INCIDENT (property damage >$25K) | REPORTABLE INCIDENT NAME | REPORTABLE H2S RELEASE | REQUIRED MUSTER | GAS RELEASE THAT INITIATES EQUIPMENT/ PROCESS SHUTDOWN | EVENT OTHER TYPE | EVENT OTHER DESCRIPTION | SPILL / RELEASE | SPILL/ RELEASE VOLUME (gallons) | OIL | DIESEL | CONDENSATE | HYDRAULIC | NATURAL GAS | OTHER | OTHER TYPE | PRODUCTION | DRILLING | WORKOVER | COMPLETION | MOTOR VESSEL | PIPELINE | HELICOPTER | OTHER OPERATION TYPE | OTHER OPERATION DESCRIPTION | EQUIPMENT FAILURE | HUMAN ERROR | SLIP TRIP FALL | WEATHER | EXTERNAL DAMAGE | LEAK | UPSET H20 SYSTEM | OVERBOARD FLUID | OTHER CAUSE | OTHER CAUSE DESCRIPTION
2006-01-05 | 1000 | Shell Offshore Inc. | N |  |  |  | GOM | 2 | GC | 65 | G05889 | 1160 | 92 | A-Bullwinkle | FIXED |  |  |  | The fire occurred on the +45 level in between the wellbays. The nearest well was approximately 15 feet. There was no other equipment with any flammable substances within 35 ft. The fire occurred when a crew was removing and replacing grating. The area was barricaded with temporary handrails due to the grating being removed and replaced, thus resulting in temporary holes in the deck. A fire retardant blanket was placed around the immediate vicinity of the hot work and draped over the temporary handrails in an effort to contain and eliminate any sparks from leaving the immediate work location. The fire on the burning torch inadvertently contacted the fire blanket. This resulted in very small fire on the blanket which was immediately extinguished. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-01-13 | 1320 | ExxonMobil Oil Corporation | N |  |  |  | GOM | 2 | GC | 18 | G04940 | 700 | 80 | A | FIXED |  |  |  | Waste heat piping installation that may have contained a small amount of oil from a flange gasket caught fire due to excessive heat. The flame was approx. 2 inches high. A waste heat gate actuator failed to fully divert the waste media causing the excessive heat. The flame was immediately extinguished with a fire hose. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-01-13 | 1210 | Unocal Exploration Corporation | N |  |  |  | GOM | 4 | HI | 178 |  | 52 | 20 | B | WP | PRIDE KANSAS | JU |  | THERE WAS A SMALL FIRE IN THE ENGINE ROOM THIS DATE AT 1210 HOURS. SOME BLACK SMOKE WAS NOTED, AND THEY SHUT DOWN THE ENGINE IN LESS THAN ONE MINUTE. NO INJURIES, NO POLLUTION, AND NO SIGNIFICANT EQUIPMENT DAMAGE OCCURRED. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | Y | Unknown at this time
2006-01-14 | 300 | Freeport-McMoRan Energy LLC | Y | N |  | 2006-03-13 | GOM | 1 | MP | 299 | G01316 | 209 | 15 | FP | FIXED |  |  |  | At approximately 3:00 a.m. the forced draft, fire component (EAL-420) for the Hot Oil Heater (HOH) experienced a shutdown. The PMI Operator was working the night shift. When the shut-in occurred, the PMI Operator woke up the PMI Lead Operator to inform him of what happened. Both men then assembled at the Instrument Control Panel for the HOH units. The Lead Operator observed that an indicator for the Pressure Safety Low on the Fuel Gas was "flagged" red. With this being known, they initiated the "Startup Procedures for the Hot Oil Heater 420" for the downed unit. The Lead Operator indicated that he moved the control setting on the Temperature Control Valve (TCV) down to approximately 100º F. He then walked to the north side of the HOH unit and closed the manual valves (A2 and A2R) on the main fuel line from the Fuel Gas Scrubber for the entire facility. Then he closed the two manual valves on the lines under the HOH unit that supply fuel to the smaller burners. He then closed the manual valves on the upstream side of the TCV. This action would have prevented gas from going to the Main Burner. At this point Relay # 1 (again referring to the Start-Up Procedures) was actuated, the button to start the blower motor was pushed and Relay # 3 was actuated to start the timing sequence for the system purge. After the timing circuit "timed out", steps were taken to light the Pilot Burner. All of the steps in the Procedure being followed to this point, he then re-opened the manual isolation valves (A25 and A2R) on the main fuel line located on the north side of the HOH unit. The igniter button (step 9, number 5 on the panel) was pressed. The igniter enabled the Pilot Burner to ignite and the PMI Operator observed a subsequent reading of 10 volts on the panel-mounted voltmeter. At this point he indicated to the Lead Operator that the lighting of the Pilot Burner had been completed, indicating a satisfactory flame on the pilot. Relay # 7 was then actuated. This action opened the two SDVs on the fuel gas to the Main Burner. The Lead Operator "cracked" opened the by-pass valve for the TCV. This manual action would allow a small, controlled amount of fuel gas to go to the main burner. When this action was performed, the PMI Operator indicated to Lead Operator that the panel-mounted voltmeter had dropped to 0 volts indicating a low or no pilot condition. The Lead Operator closed the by-pass valve he was controlling and moved to the north side of the HOH unit to manually close the two main valves (A2S & A2R). It is at this point that the explosion occurred. | 0 | [5 empty] | N | Y | Y | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | Y | N | N | N | N | N | N | Y | Failure to follow procedures
2006-01-19 | 1620 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 3 | EI | 252 | G00983 | 150 | 49 | I | FIXED |  |  |  | A small tarp fire occurred while a construction crew was cutting a hatch way to remove a potable water tank from a lower deck. Hot slag fell on one of the tarps that was being used as a barrier, resulting in ignition and a small fire. The fire watch extinguished the small fire immediately with firewater. No injuries or pollution were reported as a result of the incident. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | Y | Construction Work | N | Y | N | N | N | N | N | N | N
2006-02-05 | 1100 | Pogo Producing Company | Y | N |  | 2006-04-04 | GOM | 1 | MP | 61 | G16493 | 91 | 20 | A | FIXED |  |  |  | On February 5, 2006, at Main Pass 61-A a "Fire" incident causing a total shut-in of production occurred at 10:58 a.m. On the morning of the fire an alarm sounded at 10:43 a.m., Level Safety High "LSH" glycol separator. The second alarm sounded with a Burner Safety Low "BSL" at 10:58 followed by a fire alarm. At 10:58 the platform production process shut down by means of a Temperature Safety Element "TSE" caused by the fusible safety system. Also an Emergency Shut Down "ESD" was activated at 10:59 a.m. The fire alarm was sounded by one of the construction foreman working in close proximity to the Glycol unit that was on fire. At this point he and other personnel extinguished the fire with dry chemical and then started cooling the system with water. During this state other peripheral flames migrated via water pushing enflamed liquid into the open drain system. The personnel that extinguished the fire also prevented the possibility of a secondary ignition. No other physical damage was observed concerning the drainage system. After the fire was extinguished all non-essential personnel mustered and were evacuated safely from the facility. No pollution or injury are known or reported. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-02-06 | 230 | ExxonMobil Oil Corporation | Y | N |  | 2006-04-10 | GOM | 1 | WD | 73 | G01083 | 168 | 22 | A | FIXED |  |  |  | 'At the time of the incident normal production operations were being conducted and the night operator had been in the compression building at approximately 1:30 AM. At approximately 2:20 AM on February 6, 2006, an audible process alarm at the West Delta 73 Platform was triggered by the # 5 compressor shutting down. The night operator on duty proceeded to the compression building to investigate the cause of the shut down. Upon arrival at the building, the night operator witnessed smoke, visible fire and the dumping of the CO2 system inside the building. The night operator immediately notified the quarters building to sound the general alarm and activated the Emergency Shut Down (ESD). Everyone onboard (approximately 68 personnel) mustered as required and a team of 5 employees was dispatched to assist the night operator with extinguishing any remaining fire and smoldering debris. The safety systems performed as designed. CO2 in combination with the ventilation system shut down and the ESD was able to suppress the bulk of the fire. Two, of the five compressors in the building, as well as, control panels, cables, wall/ceiling insulation, gantry beams and turbine air intakes were badly damaged. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-02-08 | 1500 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 5 | VR | 24 | G03543 | 28 | 8 | 10 | CAIS |  |  |  | The intial report was that operators were attemping to do a downhole valve check on the #10 well. The tree cap was removed and the operator was climbing down from the tree when he lost his balance and grabbed the crown valve handle. The valve opened enough to cause gas to escape to the atmosphere and blow against the underside of the heliport causing a small fire. The heliport sustained minimal fire damage and there was no injury to personnel. An MMS inspection team investigated the incident on February 9, 2006 and determined that poor judgment by the operators to remove the tree cap and utilize the crown valve instead of the needle valve to bleed down the well contributed to the cause of the fire. Final report. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-02-10 | 1100 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 1 | MP | 300 | G01317 | 210 | 15 | B | FIXED |  |  |  | Welding caused hot metal to melt polyfoam being used for TSE service. Instruments gas inside polyfoam ignited causing a flash fire. Platform ESD. No injuries. They will fax or emial the RCA. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | Y | Construction | N | Y | N | N | N | N | N | N | N
2006-02-13 | 1600 | Eni Petroleum Exploration Co. Inc. | N |  |  |  | GOM | 1 | EW | 921 | G12142 | 1700 | 72 | A-Morpeth East | MTLP |  |  |  | A brief flash fire occurred while restarting the HP compressor. The fire was immediately extinguished. There was no damage and no injuries. Fuel source was the lubricator for the starter. Ignition source was an engine backfire escaping from the engine exhaust. The fill plug had worked loose and allowed the flash associated with the backfire to escape underneath the blanket, in the vicinity of the starter. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-02-19 | 1045 | SPN Resources, LLC | N |  |  |  | GOM | 4 | HI | A 309 | G02735 | 210 | 104 | A | FIXED |  |  |  | A small fire occurred inside the gerator housing, and the UV detector shut in the platform. The fire was extinguished in about five seconds. No injuries and no pollution was reported. MMS will investigate when weather permits. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | Y | Unknown at this time
2006-02-22 | 825 | Marlin Energy Offshore, L.L.C. | Y | N |  | 2006-04-12 | GOM | 2 | ST | 21 | 00263 | 40 | 3 | 116 | WP |  |  |  | On February 2, 2006, work was being performed on Platform #116. A pre job safety meeting was held, JSA completed, the Hot-work permit was issued, and a gas detector was used, finding no traces of gas at flanges. The well had been shut in since the storm and the crew began there assigned task. Certain individuals were assigned to break the nuts and remove a 2 inch ball valve for the gas lift line that penetrated the cellar deck. The crew understood that the platform had been shut in since the storm and confirmed that the check valve and block valve behind the 2 inch valve were closed. The bolts had been broken and prior to having removed the valve, the crew was stopped so that they could allow for the welder to cut the damage grating on the production deck. This was above the two inch valve. A fire watch and a man with the gas detector were posted on the cellar deck. As the grating was being cut, escaping gas from the 2 inch valve ignited and was immediately extinguished with no injury or damage | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-02-27 | 300 | Energy Partners, Ltd. | N |  |  |  | GOM | 2 | ST | 26 | G01870 | 58 | 26 | C | FIXED |  |  |  | A bushing and bearing failure in the VRA compressor engine oil pump caused overheating and the upper gasket to leak from the upper half onto the hot outer bottom half, causing the fire. One operator called "fire" on the radio, and killed the engine and fuel gas. He then used a 30lb dry chemical fire extinquisher to douse the fire. Another operator activated the ESD, while another hit the fire alarm. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-03-01 | 1620 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | ST | 130 | 00456 | 159 | 27 | A | FIXED |  |  |  | While welding on grading, on the top deck of platform, welding slag fell on the welding blanket and caught fire. The blanke was quikly put out. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-03-03 | 800 | SPN Resources, LLC | N |  |  |  | GOM | 1 | WD | 86 | G02934 | 143 | 5 | A | FIXED |  |  |  | Employee witnessed the gas compressor shut down on automatic alarm of a 3rd stage scrubber. Employee then began to bleed the liquid out of 3rd stage scrubber through a 1/2" ball valve located on the bottom of the high pressure sight glass located on the side of the scrubber. (A 1" ball valve on the bottom of the LSF Fisher 2lOO control bridle was found open during the investigation after the fire.) As the liquid was flowing out of the vessel through the open valve, the amount of liquid as well as the volume began to slow in rate. The employee went over to the pneumatic control panel for the gas compressor and cleared the alarm and started the engine. The engine rolled over and started running on its own. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-03-03 | 1430 | Eni Petroleum Co. Inc. | N |  |  |  | GOM | 2 | GC | 473 | G05922 | 3842 | 115 |  |  | DIAMOND OCEAN AMERICA | SS |  | While a rig hand was testing the HPU, a valve had been inadvertently left open and leaked oil down the crane leg onto #3 engine exhaust piping below causing a flash fire and smoke. Fire was put out and situation secured. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-03-03 | 2130 | W & T Offshore, Inc. | N |  |  |  | GOM | 3 | EI | 95 | 00046 | 23 | 25 | F | FIXED |  |  |  | A small flash fire occurred during a compressor start-up operation at W&T Offhsore, EI 95 platform. When the compressor was started the engine back-fired causing a small flash fire to ignite in the engine exhaust. The small flash fire was immediately extinguished by platform personnel. Fire alarms were sounded and all onboard responded by reporting to their designated location. All wells had been shut-in 15 hours prior to the start-up. There were no injuries or pollution as a result of the incident. Accident Investigation Form 2010 will not be completed. FINAL REPORT | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | Y | Conpressor back-fire | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-03-04 | 1635 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | SS | 266 | G01034 | 179 | 50 | A | FIXED |  |  |  | While welding a latter cage onto a glycol tower a small leak from a 2 inch valve occurred and caught fire from falling slag. The fire was quickly extinquished with a water bottle. Note: the area had been sniffed before welding began. They had a fire watch with a hand held fire entinquisher and they had completed a JSA and a Hot Work Permit. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-03-06 | 1130 | Samson Contour Energy E&P, LLC | Y | N |  | 2006-05-04 | GOM | 5 | VR | 218 | G01142 | 120 | 58 | B | FIXED |  |  |  | AS THE WELDER AND WELDERS HELPER WERE PERFORMING HOT WORK ON THE TOP DECK ( PRE FAB HANDRAILS) SLAG FELL TO THE BOTTOM DECK AND IGNITED A 1/4 FULL TANK OF METHANOL, CAUSING IT TO EXPLODE. THIS RESULTED IN A FLASH FIRE, FOLLOWED BY SEVERAL SMALL FIRES INVOLVING RESIDUAL PLASTIC AND PAPER PRODUCTS. THE EXPLOSION AND RESULTING FIRE CAUSED BURNS TO TWO OF THE WELDERS. THEY WERE EVACUATED TO SHORE FOR TREATMENT. BOTH WRE ADMITTED FOR TREATMENT, WHICH RESULTED IN LOST TIME. | [6 empty] | N | Y | Y | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | Y | PLATFORM SHUT IN SINCE RITA | N | Y | N | N | N | N | N | N | Y | INCORRECT PREP FOR HOT WORK
2006-03-20 | 1530 | Newfield Exploration Company | N |  |  |  | GOM | 5 | WC | 291 | G04397 | 43 | 36 |  |  | ROWAN JUNEAU | JU |  | A Baker Hughes Drilling Fluids conveyance vacuum motor on top of the shaker house caught fire and was extinguished with the use of dry chemical. The operators report states that "the fire appeared to have started when the excess bundle of electrical cable vibrated up against vacuum exhaust. Although the conveyance vacuum motor was sent in, an investigation into the incident will be conducted on 3-21-06. Our investigation revealed no damage to the rig and as stated above the power cord for the vacuum unit rubbed against the exhaust and caught on fire. The roughneck noticed the smoke and alerted the rig personnel and extinguished the fire with a handheld fire extinguisher. Final report | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-04-01 | 1112 | Pogo Producing Company | N |  |  |  | GOM | 1 | MP | 61 | G16493 | 102 | 20 | B | WP |  |  |  | Small fire flash from the stack on Glycol system extinguished with dry chemical and fire water system. No injuries or pollution. Damage to stack only. MMS will investigate. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | Y | Will investigate
2006-04-02 | 1200 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 1 | MP | 41 | 00374 | 51 | 14 | B | FIXED |  |  | 10149 | Sparks and slag from installation of grating on the production deck ignited gas leaking from a the pipeline flange 20 feet below. Fire watch spotted the small flame, notified personnel and extinguished the fire using a portable fire extinguisher. Found very small leak in the flange. Isolated the line (installed LO/TO) and began bleeding the line down so that the flange can be tightened to stop the leak. No injury, Pollution and no damage. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | Y | N | N |  | N | N | N | N | N | Y | N | N | Y | Welding
2006-04-02 | 1630 | Dos Cuadras Offshore Resources, LLC | N |  |  |  | PAC | 8 | 6B | 4861 | P00216 | 205 | 9 | GILDA |  |  |  |  | During removal of old water inj wiring in control rm PLC cab, PLC5 circuit #17. Circuit breaker LPB #17 was turned off without incident. Electrician removed wire #17 then removed wire #17n, the neutral wire (not of proper color) on the neutral bar in LPB lighting panel. As soon as #17n was removed, the PLC began to smoke. The electrician attempted to replace wire #17 back on the terminal block and the wire arced. The PLC caught fire & began to burn. The fire was extinguished platform shut in. APCD and MMS was notified. Cause was a light over chem pmp skid was full of water, when #17n was removed, ballast shorted causing the PLC to melt & start a fire. Neutral system for all circuits being conducted. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-04-08 | 1700 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 3 | EI | 252 | G00983 | 151 | 49 | C | FIXED |  |  |  | Smoke was observed to be coming from the air conditioner unit inside the galley of the living quarters and an investigation determined that a small flame was inside the unit. The flame extinguished itself shortly after the power was turned off. The small fire was started when an electrical breaker inside the unit shorted out and ignited a rubber boot that protects the wiring to the compressor. There were no injuries and no pollution as a result of the incident. An accident investigation form 2010 will not be completed. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-04-11 | 1400 | Stone Energy Corporation | Y | N |  | 2006-04-17 | GOM | 5 | VR | 256 | G01153 | 180 | 88 | E | FIXED |  |  |  | As the welder was cutting rail guides off of a temporary 70 ton crane, the oxygen side of a cutting hose parted approximately one and a half inches behind the torch assembly. This mixture ignited and burnt the welder's glove and hand. The crane operator that was watching the operation grabbed the hose about 12 inches behind the torch assembly and "kink" it to stop the flame. Two other hands made their way to the bottle rack and turned off the supply to the hose. At this time the crane operator let go of the "kink", and in doing so, the excess pressure that was left on the hose exhausted and ignited, burning the crane operator's hand and wrist area. The fire watch extinguished one 30 pound extinguisher and put out remaining flame. Both injured persons were given first aid on site and flown to a hospital. MMS inspectors on site condemned the hose, regulators, torch assembly and all associated fittings. Stone will send all this equipment in to get tested and will provide MMS with their findings. At this time probable causes include, but are not limited to, faulty hose, faulty check valves on torch assembly, and faulty regulators causing overpressure of hose. The hose is rated for 150 psi. Oxygen bottles under normal conditions may contain up to 2000 psi. Propylene bottles can contain up to 300 psi. Regulators were set that morning at 10 psi for the Propylene and 50 for the oxygen. The hose was in new condition. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-04-13 | 730 | Hunt Petroleum Corporation | Y | N |  | 2006-06-08 | GOM | 1 | MP | 101 | G22792 | 56 | 20 | D | FIXED |  |  |  | On the morning of April 14, 2006, a contract production operator and two contract mechanics boarded the facility. The condensate pump PAX-0340 had been out of service for an extended period of time and the engine wouldn't start. The mechanics were assigned to fix everything that was wrong with it, make it right, and make it run. In the process of troubleshooting the engine, while checking the compression on one of the engine cylinders a flash fire occurred burning both mechanics and the operator, who had walked up to check on their progress. The operator ensured that the fire was out and that the platform had shut in on an ESD. The operator notified his supervisor, then they immediately boarded the helicopter and flew to West Jefferson Hospital. Upon medical examination, it was determined that the operator and one of the mechanics had suffered minimal first degree burns to their faces. The other mechanic suffered burns to his face and arms, first degree and two small second degree areas. The foreman dispatched another operator to visit the facility, double-check that the platform was shut in, and verify that there was no pollution. The operator was instructed to not touch anything, pending investigation the next morning. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-04-23 | 1948 | BP Exploration & Oil Inc. | N |  |  |  | GOM | 2 | GC | 743 | G15607 | 6675 | 123 |  |  | GSF DEVELOPMENT DRILLER II | SS |  | The GSF Development Driller II semi-submersible drill rig was conducting a well test and flow back to barge Massachusetts when a small fire occurred in an electrical junction box in the generator room on the barge. The ESD was activated and all operations were shut down on the barge, rig and the well. The fire was extinguished quickly and no damage was observed and power was restored on the barge. The Coast Guard has been notified and there were no injuries and no pollution. The fire is under investigation by BP and Moran. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-04-27 | 530 | Chevron U.S.A. Inc. | Y | N |  | 2006-06-26 | GOM | 3 | EI | 360 | G02323 | 307 | 102 | C | FIXED |  |  |  | At approximately 05:30 am, a contract rigger exited the galley east door and proceeded around the west side of the quarters looking for co-workers. When rounding the corner of the quarters, he observed smoke coming from the front of the generator building. The contract rigger approached the area where the smoke was coming from to determine the source of the smoke. Upon determining that the fire was apparently in the generator room, he immediately returned to the galley to alert all platform personnel that there was a fire. The contract rigger proceeded back to where he saw the smoke next to the generator building and grabbed a 30 lb handheld chemical extinguisher. Two more contractors proceeded to the area of where the smoke was seen. While passing by one of the firewater reels located on the top deck above the fire, the contractors grabbed the hose and began to spray the fire. The contractors used a combination of dry chemical and firewater to spray on the flames coming from penetrations in the solid decking. The contractors quickly determined that the fire could not be extinguished from the top deck since the source was below the solid deck. Two of the contractors proceeded downstairs to locate and attempt to extinguish the fire, while the third contractor went back to the quarters to ensure that the remaining personnel were aware of the severity of the situation. The third contractor proceeded to the second deck and was followed by 2 Chevron platform operators. They observed the contractors spraying water on piping and flames. Flames were approximates 8-10 feet in length and encompassed the spacing between the overhead piping and underside of the top deck. Water spray from one of the main fire monitors was extinguishing burning debris but did not appear to be extinguishing the source of the fire. Chevron platform operators activated the platform ESD shutting in all production process equipment. A Chevron platform operator informed members of the construction crew that the fire water pressure would return once the emergency generator was placed on-line. The fire water pump did not come online when the emergency generator was placed online. One contractor grabbed a 30 lb portable extinguisher and proceeded up the adjacent stairway landing onto the production vessel deck and sprayed dry chemical onto the fire from approximately 15 feet. The fire began to subside immediately and was extinguished. One of the contractors went back upstairs to the escape capsule muster station to announce that the fire had been extinguished. A contractor was designated to maintain a fire-watch. He proceeded to the lower deck with a fully charged extinguisher to monitor the area. Chevron operators then returned to the living quarters and began the notification process. Two of the contractors remained with the fire-watch, monitoring the area for approximately one hour. Chevron operators gave the all clear for all employees to leave the area. The entire event lasted for approximately 3 and 5 minutes. At the time of the incident there were 12 platform personnel onboard. Upon initial notification of the fire, the galley crew activated the platform alarm system, cleared quarters, and began mustering personnel at the escape capsule. The construction foreman grabbed 2 portable radios, and contacted the field boat informing them of the platform fire. The boat arrived on location within 7-8 minutes. Prior to the fire all personnel on the platform had received orientation on the location of all firefighting equipment, life saving equipment, and emergency procedures. This contributed to the orderly response for extinguishing the fire and preparation to evacuating the platform. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-04-28 | 1045 | Bechtel Energy Partners Ltd. | N |  |  |  | GOM | 2 | ST | 41 | G24954 | 72 | 18 | B MOPU | MOPU |  |  |  | While pouring hydrocarbons from a plastic cylinder into a grounded 5 gallon metal bucket a flash fire occurred. The fire could have been caused by static electricity. The flash fire was immediately extinquished with a 30lb dry chemical unit. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-04-30 | 200 | Apache Corporation | N |  |  |  | GOM | 1 | MP | 151 | G02951 | 174 | 10 | A | FIXED |  |  |  | A portable diesel air compressor caught fire and was extinguished immediately. No injuries. No pollution. The P/F is in process of P&A Wells and take P/E out of Service. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-05-09 | 300 | The Houston Exploration Company | N |  |  |  | GOM | 5 | VR | 370 | G02275 | 300 | 99 | C | FIXED |  |  |  | Construction was in the process of conducting hurricane repairs, which included welding around the helideck which is made out of wooden boards. The welding and burning activities were shut down at ~1900hrs. on May 8, 2006 and the fire was discovered at 0300 hrs. on May 9, 2006. The fire was extinguished without injury to personnel or damage to other areas of the platform. Final Report | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-05-13 | 1120 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 1 | MP | 41 | 00374 | 51 | 14 | B | FIXED |  |  |  | Small fire: Started exhaust vent on compressor caught fire. Minimal damage to electrical wire and insulation burnt. Contact hand slipped while tring to shut off starter. MMS will investigate. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | Y | return compressor to service | Y | N | N | N | N | N | N | N | N
2006-05-13 | 2030 | Arguello Inc. | N |  |  |  | PAC | 7 | SM | 464 | P00450 | 430 | 7 | HIDALGO | FIXED |  |  |  | RIG 90 DRILLING CREW WAS PREPARING TO RUN TUBING INTO WELL C-15. AT APPROX 8:30 PM, SMOKE & FIRE WAS NOTED IN THE DRAW WORKS B MOTOR. DRILLER SHUT DOWN MOTOR & FIRE WENT OUT. ELECTRICIAN CHECKED MOTOR & CONNECTIONS & FOUND NO INDICATION FOR THE FLAMES & RESTARTED MOTOR TO EVALUATE. AGAIN, SMOKE APPEARED & FLAMES WERE SEEN INSIDE AIR EXHAUST. MOTOR WAS IMMEDIATELY SHUT DOWN & FLAMES EXTINGUISHED. THE MOTOR WAS RECENTLY REBUILT & HAD BEEN IN SERVICE FOR APPROX 3 WKS. IT IS CURRENTLY LOCKED OUT & RED TAGGED. IT WILL BE RENOVED & SENT TO SHOP WHERE IT WAS REBUILT TO DETERMINE THE CAUSE OF THE FIRE. A 3RD PARTY EXPERT WILL BE DEPLOYED BY PXP TO WITNESS THE TEARDOWN & ASSIST IN THE INVESTIGATION. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | Y | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-05-18 | 815 | Marlin Energy Offshore, L.L.C. | N |  |  |  | GOM | 2 | SS | 354 | G15312 | 477 | 75 | A | FIXED |  |  |  | An open ended section of a 4 inch previously removed riser, caught fire when the welder tried to cut the piping to remove it. The M/V Kay Ann was called over with a fire monitoring system to extinguish the flames. The construction crew involved held a safety meeting to discuss this incident and prevent future incidents. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-05-19 | 830 | Marlin Energy Offshore, L.L.C. | N |  |  |  | GOM | 2 | ST | 21 | 00263 | 50 | 5 | 63 | WP |  |  |  | As part of the removal procedure for ST 21 #63, a welder was cutting on an open ended section of riser. Preliminary indications are that heat generated by this operation caused a paraffin build-up inside this open ended pipe to gasify, release and ignite. The fire lasted approximately 10 minutes and was extinguished by the marine vessel Charlie T, which was on location. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | Y | Plug & Abandonment Operations | N | Y | N | N | N | N | N | N | N
2006-05-20 | 1440 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 1 | MP | 300 | G01317 | 210 | 15 | B | FIXED |  |  |  | Grand Isle Shipyard construction crew was welding a deck extension on an upper deck off to the side of the compressor building. They thought they were tarped enough to contain all sparks. The compressor building wall had a hole in the tin from the hurricane. The sparks went in the wall hole and ignited a box of filters. The platform TSE was triggered and the structure shut-in. The fire was then put out using dry chemical fire extinguishers. There were no injuries or property damage. We will have GIS to come out first thing in the morning to conduct a full RCA of the incident. We estimate material damage to be less than $500. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-05-25 | 1755 | Maritech Resources, Inc. | N |  |  |  | GOM | 3 | SM | 48 | 00786 | 107 | 45 | B | FIXED |  |  |  | A small flash fire occurred while repair was being performed on a walkway around well B-6. A small amount of undetected gas from the well was ignited when the welder was using a cutting torch around the wellhead. Well B-6, is non-producing and is currently in a plugged status. A member of the work crew immediately extinguished the flash fire using one of the welder gloves. All work was performed in accordance to Maritech welding and burning plan. No pollution or injuries occurred as a result of this incident. No accident investigation 2010 will be completed. FINAL REPORT | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-05-31 | 430 | Petrobras America Inc. | N |  |  |  | GOM | 3 | GC | 247 | G23282 | 1775 | 151 |  |  | DIAMOND OCEAN VOYAGER | SS |  | A small fire occurred on the No. 8 generator. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-06-07 | 1130 | PANACO, INC. | Y | N |  | 2006-08-04 | GOM | 4 | EB | 165 | G06280 | 863 | 90 | A | FIXED |  |  |  | While preparing to transfer methanol from a 500 gallon stainless steel chemical transporter (tank tote) to a poly storage tank (plastic tank), the crane operator employed by Island, lifted the tank tote with methanol to gravity feed it into a poly storage tank on the top deck. When the tank was raised to a height of approximately seven feet, two Multi-Chem employees observed methanol spraying out of the hose at a point half way down it's length . The spray was directed outboard, towards the handrail, and onto the lower deck, around the gas and air compressors . The Island crane operator began to lower the tank towards the deck, so that the Multi-Chem employees could close the valve on the tank tote. The methanol that sprayed on to the lower deck was ignited by the heat of the exhaust from the compressor and spread to the top deck. In bright sunlight, burning alcohol produces only a very light blue flame with no smoke and is not easily seen. Before the tank tote reached the deck, both Multi Chem employees felt intense heat in and around the area at the base of the crane and the immediate area around the tank totes. One Multi Chem employee began kicking tank tote valves closed and in turn broke the sight glass on one of the tank totes, spilling methanol onto the deck. At this time, production personnel on the lower deck became aware of the fire in the vicinity of the gas compressor skid. The fire alarm sounded and the employees initiated the ESD from the upper deck. By this time, the fire had spread across the southeastern portion of the upper deck. PSV's on two other chemical tank totes began relieving, and fire was reported on top of one tank tote. The eight persons on board, two Island, four Baker, and two Multi Chem, formed a fire brigade and fought to contain and extinguish the fire using dry chemical and fire water on the lower deck and then moved to the upper deck to fight the fire. Now they were fighting two fires. The fire was extinguished on the lower deck around both the air and gas compressors. The crew then moved to the top deck to fight the fire around the chemical storage area. After expending twenty-two 30-lb.hand-held and two 125 lb. wheel units and using two fire monitors for thirty minutes, the fire was out and water was sprayed for another hour. The injured man received second-degree burns on the lower part of one of his legs while shutting the site glass valve off on the paraffin inhibitor. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | Y | N | N | N | N
2006-06-09 | 115 | Eni Petroleum Co. Inc. | N |  |  |  | GOM | 2 | GC | 254 | G07049 | 3248 | 93 | A-Allegheny TLP | MTLP |  |  |  | An overflow of a diesel purge tank flowed onto the insulation of the diesel engine exhaust which caused a fire. One hand held fire extinquisher and a 50lb wheeled unit were used to extinquish the fire. The crew did muster but did not evacuate. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | Y | Hi-Bi Level Alarm
2006-06-12 | 2100 | Williams Field Services - Gulf Coast Company, L.P. | N |  |  |  | GOM | 1 | MP | 261 | RUE 22084 | 299 | 80 | JP | FIXED |  |  |  | The operator saw smoke coming from the #2 gas generator package and suspected equipment failure. The diesel generator was immediately started and the #2 gas generator was shut down. When the operator opened the door of the generator package a small flame erupted from the turbo area of the generator driver. This flame was immediately extinguished with a 20# fire extinguisher and no damage occurred. Examination of the generator revealed that a fitting was cracked on a ½” oil line, causing oil to spray onto the engine turbo. This oil caught fire when the operator opened the door of the unit. All fittings of this nature were examined on the generator #2 and the other two generators for signs of deterioration. No deterioration was observed. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-06-12 | 1845 | Dos Cuadras Offshore Resources, LLC | Y | N |  | 2006-09-20 | PAC | 8 | 6B | 4861 | P00216 | 205 | 9 | GILDA | FIXED |  |  |  | WELDER WAS REPAIRING SPLASH GUARD ON GALLEY STOVE W/ARC WELDER & DID NOT RUN GROUND STRAP. CONDUIT ON WIRE TO STOVE GOT HOT & MELTED THE WIRE INSULATION & CAUGHT FIRE. THE FIRE WATCH SAW THE SMOKE & STOPPED WELDER & EXTINGUISHED THE FIRE. THIS ALSO CAUSED A GROUND FAULT & KICKED THE MCC1 BREAKER IN THE PDM & SHUT DOWN PLATFORM WHEN IT SWITCHED TO EMERGENCY POWER. C/A; HOT & SAFE WORK PERMIT SYSTEM ADDRESSES PROPER GROUNDING OF EQUIP. THE PERMITS WILL BE CHECKED & VERIFIED BY OPS PERSONNEL TO ENSURE SAFETY ITEMS ARE ADDRESSED ON THE HOT WORK & SAFE WORK PERMIT ARE IN PLACE PRIOR TO SIGNING TO BEGIN WORK. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | Y | MAINTENANCE | N | Y | N | N | N | N | N | N | N
2006-06-13 | 1235 | El Paso Production Oil & Gas USA, L.P. | N |  |  |  | GOM | 3 | EI | 364 | G19799 | 360 | 81 | A | FIXED |  |  |  | A small fire occurred as the electrian was trouble shooting gas generator panel problems. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-06-20 | 1200 | Kerr-McGee Corporation | N |  |  |  | GOM | 2 | SS | 233 | G01528 | 128 | 42 | B | FIXED |  |  |  | Falling welding slag ignited the blanket gas over the sump tank. The fire was extinquished with one handheld dry chemical fire extinquisher and the deluge system. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-06-24 | 1500 | Apache Corporation | N |  |  |  | GOM | 2 | ST | 205 | G05612 | 161 | 40 | B | FIXED |  |  |  | While replacing corroded bolts on a section of pipe, a flash fire occurred in the area of the flange. Bolts were being removed with a cutting torch. A 20lb hand held dry chemical fire extinquisher was used to extinquish the fire. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-06-24 | 130 | BP Exploration & Production Inc. | N |  |  |  | GOM | 2 | GC | 743 | G15607 | 6675 | 130 |  |  | GSF DEVELOPMENT DRILLER II | SS |  | A wiring fire occurred in the aux-panel in the Rig's engine room. No actual fire just smoldering wiring. It tripped the rooms smoke alarm. No extinquisher used. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-06-25 | 1200 | Merit Energy Company | N |  |  |  | GOM | 2 | SS | 198 | G12355 | 100 | 60 | J-PRD | FIXED |  |  |  | While conducting hot work, a flash fire occurred in the containment skid surrounding the sump pump. When the fire was noticed, the supervisor sounded the alarm and the remaining platform personnel secured life jackets and proceeded to the muster station. Cutting sparks fell in the sump tank skid on the side opposite of the sump and the fire quickly spread. The fire watch and 6 other crew members proceeded to extinguish the fire using 7 fire extinguishers. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-06-27 | 210 | Shell Oil Company | N |  |  |  | GOM | 1 | MC | 807 | G07963 | 3800 | 67 | A-Mars TLP | TLP |  |  |  | A small amount of diesel sprayed on the Turbine generator causing a small fire. Mustered personnel and Platform shut-in. Fire was put out immediately no injuries, damage or pollution. The diesel leak was due to a cracked valve in the diesel fuel line for the gererator. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-07-06 | 1050 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 3 | SM | 78 | G01210 | 139 | 64 | B | FIXED |  |  |  | A flash fire occurred on the exhaust system of a turbine compressor. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-07-09 | 145 | Arguello Inc. | Y | N |  | 2006-12-26 | PAC | 8 | 6A | 5585 | P00315 | 675 | 7 | HARVEST | FIXED |  |  |  | FIRE ALARM WAS ACTIVATED AT 0145 IN BUILDING 332 CIU (LOCATION OF FIRE SAFETY'S). LOCATION OF FIRE WAS LACT CHARGE PMP C. OFD (OPTICAL FLAME DETECTORS) & FUSIBLE LOOPS AT PMPS INITIATED DELUGE & PLT SHUTDOWN SYSTEM. SPECIFIC LOCATION OF FIRE WAS IN THE SEAL AREA OF THE SUBJECT PMP. PMP SEAL FAILED, RELEASING APPROX 10 GAL(S) OF CRUDE OIL ON THE 60+ DECK. OIL WAS CONTAINED IN THE DECK DRAIN SYSTEM. ALL PERSONNEL REPORTED TO THEIR SAFE BREIFING STATIONS. NO INJURIES OCCURED. IMMEDIATE CORRECTIVE ACTION TAKEN-ISOLATED PMP W/MANUAL BLOCK VALVES. THROUGHLY CHECKED THE AREA FOR COLLATERAL DAMAGE. PERFORMED LOCK OUT/TAG OUT ON UNIT. RESTORED SAFETY SYSTEMS. RESTARTED PLT OPERATIONS. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | Y | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-07-11 | 1715 | Anadarko Petroleum Corporation | Y | N |  | 2006-08-02 | GOM | 2 | GC | 608 | G18402 | 4300 | 117 | A-Marco Polo | TLP |  |  |  | At approximately 1715 hours on July 11, 2006, a fire occurred on Fuel Gas Compressor "A". A 3\4 street ell connected to a drain valve installed on the first stage discharge bottle parted. This allowed gas to be released around the right side of the compressor. The gas was then ignited by the turbo charger on the right bank. Maintenance personnel were working on Flash Gas Compressor "B" when the released occurred. The release of the gas was heard and the concussion of the release was felt by the maintenance personnel. Upon discovering the fire, the maintenance personnel called for help and initiated a manual ESD of the gas compressor and production platform. Temperature Safety Elements (TSE'S) melted immediately and activated the deluge system. Maintenance personnel started fighting the fire, then the designated fire fighting team assembled and quickly responded to the fire. The fire was extinguished with two 150 lb. dry chemical units and two fire hose using AFFF foam. The fire team continued to apply water and foam for 30 minutes after the fire was extinguished to cool down the area. All personnel onboard responded to the alarm and reported to their assigned muster stations and were accounted for. Once the area was cleared; the foam tanks and the 150 lb. dry chemical units were refilled, checked for proper operations and returned to service. The TSE'S that were affected were replaced and the TSE loop was tested for proper operation. There were no injuries or pollution as a result of this incident. | 0 | [5 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | Y | Y | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | Y | N | N | N | Y | N | N | N
2006-07-17 | 901 | Noble Energy, Inc. | N |  |  |  | GOM | 1 | WD | 58 | 00146 | 60 | 13 | C | FIXED |  |  |  | The operator noticed smoke and a small flame on top of the reboiler. The flame was extinguished immediately and minimal damage occurred. After investigation, it was found that fluid was leaking at threads beneath PSV on vessel. The fluid accumulated between the shell and the insulation and ignited from shell temperatures. Corrective actions: The platform was shut in and the flame was extinguished. The leaking nipple threads for the PSV have been replaced and to ensure the leak was repaired properly the thread-o-let was cut out and replaced also. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-07-17 | 1440 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | SS | 209 | 00827 | 95 | 34 | A | FIXED |  |  |  | Operator noticed cigrette butt container was on fire. A piece of paper had been placed in the container, got caught in the plastic gooseneck connection of the container and went unnoticed. Burned top 4 inch of the plastic gooseneck portion of the container. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-07-18 | 840 | Plains Exploration & Production Company (PXP) | Y | N |  | 2006-08-15 | PAC | 8 | SM | 332 | P00441 | 242 | 5 | IRENE | FIXED |  |  |  | While platform was shut-down due to a loss of power from shore, an 18-inch manway on flare scrubber vessel (V-200) was opened for maintenance purposes. After the manway had been open for approximately 20 minutes, an explosion and flash fire issued from the manway, causing a minor injury to one employee and minor damage to H2S monitoring equipment in the area. The employee was treated onshore and returned to work that same day. MMS conducted investigation and subsequently issued INCs. MMS has determined that operator did not comply with 30CFR250.803 or their company safety manual. | [5 empty] | 1 | N | Y | Y | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | Y | Maintenance | N | Y | N | N | N | N | N | N | N
2006-07-20 | 1401 | Pioneer Natural Resources Company | N |  |  |  | GOM | 3 | EI | 208 | 00576 | 96 | 48 | E | FIXED |  |  |  | On July 20, 2006 at approximately 1400 hrs two pioneer employees heard the PLC alarm and the generator immediately shut down. They discovered a small fire was located on top of the reboiler near the compressor panel. The employees immediately used two portable fire extinguishers to put out the flames. Pioneer's Gulf of Mexico Foreman, Wayne Charpentier arrived on location at approx. 1500 hrs. They washed and cleaned the unit to check if the vent lines were plugged, but they were not. They also checked if something came loose inside of the insulate blankets, but found nothing. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-07-22 | 1350 | Chevron Corporation | N |  |  |  | GOM | 5 | VR | 214 | G02076 | 127 | 57 | B | FIXED |  |  |  | A welder, an employee of Danos & Curole, was welding a doubler plate on the 26" caisson of Well B-11. The welding arc burned through a thin, corroded section of metal on the caisson resulting in a small flash fire that self extinguished immediately after it started. No injury was reported. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-07-23 | 725 | Marathon Oil Company | N |  |  |  | GOM | 1 | SP | 86 | G05687 | 352 | 16 | C | FIXED |  |  |  | A fire occurred during a compressor start up. The compressor had a mechancial failure on June 27, 2006 which caused oil and coolant to enter the exhaust system. When the compressor was restarted on July 23, 2006, residual lube oil entrained in the exhaust system dripped out of the exhaust tail pipe. A Marathon employee extinguished the flame with ta 30 pound fire extinguisher. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-07-23 | 1014 | Marathon Oil Company | N |  |  |  | GOM | 1 | SP | 86 | G05687 | 375 | 16 | C | FIXED |  |  |  | Loaded compressor and started. Compressor backfired and the heat insulation blanket around piping caught fire. Put out with fire extinguisher. Shut down compressor. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-07-27 | 830 | Pogo Producing Company | N |  |  |  | GOM | 5 | EC | 335 | G02439 | 275 | 108 | A | FIXED |  |  |  | Small fire inside distribution panel box due to water leaks from storms. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | Y | N | N | N | N | N
2006-08-01 | 1500 | Apache Corporation | N |  |  |  | GOM | 1 | MP | 311 | G02213 | 250 | 33 | B | FIXED |  |  |  | When the back-up generator was started for the construction crew, a rod knocked through the block and oil from the generator started the fire. Three extinguishers were used to put out the fire. No injuries, no pollution. The generator will be replaced because of the rod. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-05 | 1500 | Maritech Resources, Inc. | N |  |  |  | GOM | 4 | HI | A 442 | G11383 | 172 | 77 | A | FIXED |  |  |  | THIS WAS AN EXTREMELY SMALL FIRE. Contruction crews were onboard preparing to remove the compressor. Welders were gouging on the suction scrubber on the drill deck, and a spark burned a piece of poly-flow tubing on top of the generator building. The fire was immediately extinguished, and the poly-flow tubing was blocked off, and the entire fuel gas system bled off. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | Y | N | N | N | N | N |  | N | N | N | N | N | N | N | N | Y | spark by welders
2006-08-05 | 1630 | Newfield Exploration Company | N |  |  |  | GOM | 5 | WC | 73 | G23736 | 40 | 15 | A | WP |  |  |  | A small electrical fire occurred in the Main breaker box of the portable diesil generator being used to supply power to the platform, The fire was extinguished by the platform personnel. Damage from the fir ewas limited to to the main breker box on the generator. No personnel were injured and the platform was not shut-in. Newfield will investigate the incident to determine the cause of the fire. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-06 | 2330 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | ST | 135 | 00462 | 111 | 50 | Q | FIXED |  |  |  | A fire occured in the Schlumberger unit generator. It was a small fire, extinguished with a 30 lb. hand held dry chemical fire extinguisher. Generator was sent in. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | Y | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-07 | 830 | Apache Corporation | N |  |  |  | GOM | 1 | MP | 140 | G02193 | 150 | 25 | B | FIXED |  |  |  | The pillar block bearing on the compressor cooling fan locked up causing the grease onthe bearing to overheat causing a small fire. The fire was extinguished with a 30lb fire extinguisher. No pollution was observed and no injuries. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-09 | 1815 | ExxonMobil Oil Corporation | N |  |  |  | GOM | 1 | SP | 93 | G01619 | 446 | 18 | A | FIXED |  |  |  | Fire was a result of the failure of a capacitor in the ballast box for the light fixture. Personnel were in the area and blew out a small flame that was burning on the capacitor insulation. There were no injuries. Damage wa minimal and isolated to one capacitor in the ballast box. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-12 | 1400 | Devon Energy Production Company, L.P. | N |  |  |  | GOM | 3 | SM | 128 | G02587 | 228 | 75 | A | FIXED |  |  |  | A tarp covering a battery box caught fire from slag dropping overhead from an operator welding. An employee working near the water maker noticed the fire on the North East bottom deck. The fire alarm was sounded and the fire was extinguished within one minute. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-08-15 | 1702 | ANGLO-SUISSE, INC. | N |  |  |  | GOM | 1 | WD | 27 | G04473 | 39 | 7 | A | FIXED |  |  |  | A flash fire occurred at the compressor starter. Gas used to turn starter. The injured person's (IP's) were standing near by during an attempt to start compressor. Gas ignited and flashed over area. Two IP's - one was treated and released on site and one was evacuated treated and released. No LTA. | [5 empty] | 2 | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-16 | 1200 | ARENA ENERGY, LLC | N |  |  |  | GOM | 4 | MI | 669 | G04065 | 96 | 23 | A | FIXED | GSF HIGH ISLAND I | JU |  | The motorman was in the area of the air compressor, and he noticed smoke coming from the general area of the air compressor. Upon investigation, he discovered a small electrical fire on the motor end of the air compressor. The small fire was extinguished immediately using one 30 lb.dry chemical. The motor is a 480 VAC, 75 horse power. Upon their investigation, the windings in the motor were the cause of the fire. There is an estimated damage amount of $5,000.00 to replace the electrical motor. There were no injuries or pollution. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-17 | 1600 | Shell Deepwater Development Inc. | N |  |  |  | GOM | 3 | GB | 426 | G08241 | 2860 | 168 | A-Auger TLP | TLP |  |  |  | A dryer located in Auger's laundry room began smoking and a small fire was observed. Operators on board immediately put the fire out and the dryer was removed from service. Shell is investigating the incident and will follow up with a report. FINAL REPORT | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-20 | 1915 | BP Exploration & Production Inc. | N |  |  |  | GOM | 1 | GI | 40 | 00128 | 86 | 14 | I | FIXED |  |  |  | Fire in trash bin on Lift Boat Dixie endeavor. Had been preforming P & A work on GI 40I. No damage. No injuries. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | Y | Lift Boat Endeavor P&A Work | N | Y | N | N | N | N | N | N | N
2006-08-20 | 1730 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | SS | 182 | G01019 | 65 | 32 | E | FIXED |  |  |  | Construction crew air compressor motor thru a rod, sprayed oil and caught fire. Motor shut down immediately. Fire extinguished with hand held. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-22 | 922 | ANGLO-SUISSE, INC. | N |  |  |  | GOM | 1 | WD | 27 | G04473 | 39 | 7 | A | FIXED |  |  |  | A small flash fire took place near one of the field compressors during the troubleshooting process. The flash extinguished itself immediately and required no control assistance. Two employee sustained small but noteworthy burns that were treated on site with first aid techniques and returen to full duty that day. No damage to compressor. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-08-23 | 900 | Energy Partners, Ltd. | N |  |  |  | GOM | 2 | ST | 26 | G01870 | 60 | 7 | C | FIXED |  |  |  | A lightning strike apparently caused a flash fire on the flare boom on this facility. The operators discharged CO2. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | Y | N | N | N | N | N
2006-08-23 | 1720 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 3 | EI | 273 | G00987 | 184 | 68 | C | WP |  |  |  | Contract crew as changing out bad grating in the well bay area on the elvated deck. A small fire, ignited by the falling slag, occurred near the casing hanger of well C-3. The 2 or 3" flame was immediately extinguished with a hand held extinguisher. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-08-24 | 900 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 3 | EI | 339 | G02318 | 260 | 83 | B | FIXED |  |  |  | Contract crew was installing a 3" valve on a gas header. The header was isolated and bled down, the blind flange was removed and the valve was being installed. There was a gas accumulation in the area of 20% LEL. The rigger/fitter, carrying a striker on his person, was assisting with the installation. An accidental spark from the striker caused ignition of the migrating gas at the valve opening. The Fire Watch was near and quickly extinguished the 1 foot flame in approximately 30 seconds | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-08-27 | 1550 | Newfield Exploration Company | N |  |  |  | GOM | 2 | SS | 58 | G07746 | 65 | 20 | A | FIXED |  |  |  | Manual drain on compressor scrubber was inadvertently allowed to flow gas which in turn traveled to the vicinty of the heater treater. This free gas was briefly ignited and self extinguished. No pollution or injuries. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-08-27 | 1515 | Newfield Exploration Company | N |  |  |  | GOM | 2 | SS | 58 | G07746 | 20 | 15 | A | FIXED |  |  |  | Production operator was draining the compressor suction scrubber manually and had gas blowby into the drain to the heater treater and ignitied. The fire was dected and put out immediately. There were no injuries, pollution or damage. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-08-30 | 741 | Magnum Hunter Production, Inc. | N |  |  |  | GOM | 1 | MP | 175 | G08753 | 137 | 65 | A | FIXED |  |  |  | Lightening stuck the flare boom and caused a small fire. The fire was extinguished immediately by Island Operating crew which flew to the unmanned facility. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | Y | N | N | N | N | Y | Lightening Stike
2006-08-31 | 1230 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | SS | 208 | G01228 | 103 | 34 | E | FIXED |  |  | 12489 | In the process of repairing pipeline due to damage from Hurricane Rita. Lay barge located newxt to platform flushed and pigged pipeline prior to welding on same. Monitored pipeline with gas detector and received no readings. A small gas pocket was in pipeline. While welding companion flange, a small fire occured. Fire was immediately extinguished with 30 lb. dry chem. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | Y | N | Y | Lay Barge | N | Y | N | N | N | N | N | N | N
2006-09-04 | 245 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | ST | 177 | G01260 | 100 | 45 | E | FIXED |  |  |  | While attempting to crank a generator, operators observed an approximately 2-inch flame emanating from a porting of the electrical circuitry. Flame extinguished with 30 lb dry chem unit. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-09-07 | 1430 | Apache Corporation | N |  |  |  | GOM | 2 | SS | 178 | G05551 | 85 | 40 | A | FIXED |  |  |  | A small generator fire was discovered at the generator enclosure. Platform personnel activated the ESD system which functioned as designed. All personnel reported to muster stations and were accounted for. The fire, which was confined to the electrical end of the generator, was quickly extinguished by personnel using 2 - 30 # dry chemical extinguishers. There were no injuries to personnel or pollution. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-09-07 | 430 | Nexen Petroleum Offshore U.S.A. Inc. | N |  |  |  | GOM | 5 | WC | 109 | G23744 | 42 | 18 |  |  | ENSCO 105 | JU |  | Unknown person threw a lit cigarette butt into a waste paper basket in the change room. It started smoking and the fire was quickly extinguished. No damages. No injury. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-09-13 | 1430 | Exxon Mobil Corporation | N |  |  |  | GOM | 3 | EI | 314 | G02111 | 235 | 87 | A | FIXED |  |  |  | Workman was using soldering torch to repair freon leak inside freezer. Gas leaked at pressure gauge and caught fire. No injuries or property damage sustained. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-09-16 | 750 | Hydro Gulf of Mexico, L.L.C. | N |  |  |  | GOM | 4 | HI | 130 | G25579 | 49 | 20 | 1 | CAIS | THE 75 | SU |  | While tripping in the hole, the rig power starte to fluctuate. Employees went to investigate and noticed the SCR room engulfed with smoke. The fire was located in the SCR room and was extinguished by 0800 hours. There were no injuries or pollution. The property damage was limited to SCR Bay no. 5 which was burned. The fire was extinguished fire with CO2 extinguishers and fire watchers were posted in various locations to prevent reflashing. All damages have been repaired and rig is back operating. Replacement parts estimate is $7,793.00. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-09-27 | 2320 | Taylor Energy Company LLC | N |  |  |  | GOM | 1 | MC | 21 | G15459 | 668 | 30 | B-SIMBA | FIXED | H&P 105 | PF |  | The mud engineer on the H&P 205 was running his night check. He started running the retort at about 10:50 pm. At 11:20 pm he took the water reading and was preparing to clean up the equipment when the retort burst into flames. He immediately unplugged all electrical equipment, knocking the retort off the counter onto the floor. He sprayed water on the flames from a distilled water dispenser bottle which was readily available and doused the fire. No damage. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-09-28 | 1045 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 5 | VR | 39 | 00206 | 12 | 9 | A-QTR | FIXED |  |  |  | Operators had started up the crane power pack to operate crane to offload the field boat. One operator was walking by the power pack and noticed smoke coming from the flange on the exhaust beneath the insulation. As he neared the power pack, he noticed a small blue flame. He shut down the unit and alerted the others on the platform. When the unit was shut down, the flame went out. The crew removed the insulation from the exhaust to investigate and found a missing plug at the flange of the exhaust and muffler. The hole was covered by the insulation. The power pack had been completely overhauled less than 1 year ago. It is evident that the insulation was installed and the unit was then painted. The paint on the insulation was charred in the area of the flange. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-09-29 | 1730 | Stone Energy Corporation | N |  |  |  | GOM | 5 | VR | 258 | G21093 | 165 | 70 | G | FIXED |  |  |  | A small fire was detected coming from the exhaust of a recently repaired 75 KW portable diesil generator. The fire was quickly extinguished with a 30 lb portable extinguisher. The unit was disconnected and sent in for repair. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-09-30 | 1915 | BP America Production Company | N |  |  |  | GOM | 1 | MC | 127 | G19925 | 5400 | 60 | A-Horn Mountain | SPAR |  |  |  | Heat trim heater was brought online for a backup in the event it would be needed due to water quality separation issues. At 1915 control room operator perceived an burning odor. Control room operator checked the MCC and found smoke coming from the trim heater panel. Control room operator immediately shut off power to the trim heater panel. I/E techs. were called to troubleshoot the problem. A loose wire on a terminal block was determined to be the cause of the smoke. Trim heater panel is out of service. Panel has been locked and tagged. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-02 | 145 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 1 | SP | 77 | G02184 | 210 | 6 | A | FIXED |  |  |  | Operator making rounds discovered a fire. He saw a visible flam coming from glycol reboiler blanket. Fire approximately 12" tall covering approximately 12"x 12". Operator notified other operator and extinguished fire with fire water hose. Stripped insulation and soaked. No damage to equipment. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-04 | 1500 | W & T Offshore, Inc. | N |  |  |  | GOM | 2 | SS | 148 | G11983 | 48 | 40 | K | FIXED |  |  |  | The dive boat M/V Patrick was located at SS 148 K supporting hurricane repair and construction operations. A small flame occurred inside the filter canister on the jet pump. The flame was extinguished with a hand-held fire extinguisher. The pump was inspected and taken out of service. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-05 | 1500 | Apache Oil Corporation | N |  |  |  | GOM | 1 | GI | 94 | G02163 | 210 | 34 | B | FIXED |  |  |  | A small fire ignited at Apache Corp.'s Grand Isle 94 B Facility on 10-5-06. During welding operations, an employee noticed sparks emanating from the armture. Upon going to investigate, he observed flames that soon engulfed the entire unit. The firewatch was near by and was able to extinguish the fire quickly. Post incident evaluation revealed minor damage to the unit with no damage to the platform. There was also no pollution noted. It was determined that the engine oil had migrated into the housing of the armature causing a short in the wiring. Sparks from the short circuit appear to have ignited the engine oil, causing the small fire. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | Y | Repair Work | Y | N | N | N | N | N | N | N | N
2006-10-06 | 1710 | Exxon Mobil Corporation | Y |  |  |  | PAC | 8 | 6A | 5374 | P00188 | 842 | 5 | HONDO | FIXED |  |  |  | Two workers were calibrating the delivery rate of a viscosity reducing chemical at the chemical injection skid when a glass graduated cylinder attached to the system exploded injuring both men. They were transported to shore for medical treatment for lacerations and to remove glass shards. One worker returned to the platform later that day, but the other remained at the hospital overnight. A third worker who did not leave the platform was treated for a cut on his hand sustained when he struck his hand on some piping after being startled by the explosion. |  | 1 |  |  |  |  | Y | N | Y | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | Y | N | N | N | N | N | N | N
2006-10-08 | 930 | Chevron Corporation | N |  |  |  | GOM | 3 | EI | 273 | G00987 | 184 | 68 | C | WP |  |  |  | Welding split sleeve on to perforated well casing after making fire prevention preparations. Small blue flame with no fuel source pressure noted and extinguished with dry chemical extinguisher. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | Y | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-13 | 1530 | Newfield Exploration Company | Y | N |  | 2007-01-31 | GOM | 4 | HI | A 531 | G02696 | 200 | 78 | A | FIXED |  |  |  | Apparently a fire in the generator room melted the T.S.E. while platform operators were answering the alarms. Someone with the paintng crew noticed smoke coming out of the generator room. The platform operators were notified. One 30 pound hand-held extinguisher and one 150 pound wheeled fire extinguisher were used to extinguish the fire. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-17 | 30 | McMoRan Oil & Gas LLC | N |  |  |  | GOM | 5 | VR | 54 | G19754 | 22 | 12 |  |  | HERCULES 77 | SU |  | Fire in Galley. The upper right hand element in the oven shorted out and caused a small fire in the oven. Fire was put out with an extinguisher. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-21 | 2330 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 1 | VK | 340 | G10933 | 157 | 70 | A | FIXED |  |  |  | When pulling out of hole with coil tubing the power pack turbine caught fire. Hit emergency kill switch. Killed engine fire went out. No damage to equipment. Sending in and getting another out. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | Y | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-22 | 1330 | Shell Offshore Inc. | N |  |  |  | GOM | 1 | MC | 809 | G05868 | 3800 | 67 | A-Ursa TLP | TLP |  |  |  | Galley employee was melting butter on the stove top in a small metal pot. When the butter came to a boil, it started to spill over onto the stove top and drip pan causing a small fire. The pot was removed from the stove top and the fire was smothered with a wet towel. The drip pan was removed from the stove and put in a nearby sink. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | Y | Galley | N | Y | N | N | N | N | N | N | N
2006-10-24 | 1145 | BP Exploration & Production Inc. | N |  |  |  | GOM | 1 | MC | 778 | G09868 | 6200 | 90 | A(Thunder Horse | SEMI |  |  |  | During welding operations a non-fire retardant tarp caught fire from hot slag. The tarp was being utilized to contain sparks during welding operations on the third export cooler deck extension. Once the fire watch noticed a small flame he immediately stopped the job and extinguished it. Fire watch made all proper notifications to control room. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | N | N | Y | Construction | N | Y | N | N | N | N | N | N | N
2006-10-24 | 1300 | BP Exploration & Production Inc. | N |  |  |  | GOM | 3 | GB | 873 | G17456 | 4704 | 156 |  |  | T.O. DEEPWATER HORIZON | SS |  | While performing hotwork in the BOP house, a piece of welding slag fell to the BOP transporter and ignited a small piece of rope. The firewatch utilized a water extinguisher to put the flame out. No damage was done. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-10-27 | 2210 | Devon Energy Corporation | N |  |  |  | GOM | 3 | EI | 120 | 00050 | 37 | 25 | CF-QTR | FIXED |  |  |  | The exhaust from a Wilden M-8 pump caught fire and was immediately extinguished using a 30# hand-held unit. It is not known what caused the small flash fire but the exhaust from the pump has been re-piped and a flame arrestor installed. The platform fusible plug located above the pump melted and initiated platform shut-in. The pump was replaced and no injuries or pollution was reported. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | Y | Small flash fire | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | Y | Unknown
2006-10-28 | 2030 | Mariner Energy, Inc. | Y | N |  | 2006-12-28 | GOM | 4 | HI | 116 | G06156 | 45 | 26 | A | FIXED |  |  |  | 'The platform was shut-in to perform maintenance. An approved welding area was assigned. Plugs were installed in drains, but apparently the drains were not washed out and filled with water. The welder began welding at the fabrication table, and a spark went into the drain causing about thirty feet of the drain to catch on fire. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-10-28 | 29 | Shell Offshore Inc. | N |  |  |  | GOM | 1 | MC | 807 | G07963 | 2933 | 67 | A-Mars TLP | TLP |  |  |  | Infrared detector went off in turbine generator 703 building. The fire panel alarm shutdown the generator. Gas response unit found no evidence of fire or smoke. Small amounts of soot were observed on ferrule gas tubing. Further analysis indicates ferrule on tubing became loose, releasing small amount of gas that ignited. All detectors functioned properly. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-29 | 1645 | Energy XXI GOM, LLC | N |  |  |  | GOM | 2 | ST | 28 | G01362 | 40 | 4 | F | FIXED |  |  |  | The #2 compressor shut in causing the venturi system to over flow sending motor oil onto the outside of venturi body causing a small flash fire. The operator sounded the fire alarm and the fire put itself out. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-10-31 | 1445 | Apache Corporation | N |  |  |  | GOM | 3 | EI | 189 | 00423 | 60 | 60 | B | FIXED |  |  |  | A welder was working on the production deck level in an area next to the gas lift header (all wells shut in) when a piece of slag/cutting was blown overboard to the plus ten sump level located 50' below. At the same time the platform sump pump kicked on and the exhaust from the pump supply gas ignited when the hot slag fell next to the pump. The onsite fire watch immediately shut down all welding and cutting operations. The fuel gas to the pump was bled off and a wet fire blanket was installed on top of the pump for the remainder of the work activities. There were no injuries or pollution as a result of the incident. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | Y | N | N | N | N | N
2006-11-02 | 1130 | Newfield Exploration Company | N |  |  |  | GOM | 3 | SM | 160 | G04433 | 279 | 83 | A | FIXED |  |  |  | While adjusting the idle speed on the compressor after changing out the compressor's carburetor, an explosion occurred blowing off the compressor's crankcase covers. Prior to the accident, the operator noticed the oil pressure drop. There were no injuries or pollution as a result of the incident. | [6 empty] | N | N | Y | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-11-03 | 900 | Apache Corporation | N |  |  |  | GOM | 2 | PL | 10 | G02925 | 35 | 5 | B | FIXED |  |  |  | While lifting the day tank for the compressor, the tank was overfilled causing the excess oil to spill on the compressor exhaust causing a small fire. The operators extinguished the fire with one 30# dry chemical extinguisher. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-11-05 | 657 | BP Exploration & Production Inc. | Y | N |  | 2006-01-31 | GOM | 1 | MC | 777 | G09867 | 6037 | 98 |  |  | T.O. DISCOVERER ENTERPRISE | DS |  | At 0656 hours on November 5, 2006, maintenance personnel near the port aft high voltage switch gear room heard an abnormal noise/buzzing with light smoke in the space. During their investigation of the space, they heard a louder pop and found the port harmonic filter had blown its three fuses. The fuse material caused a small fire due to the fuse slag near the base of the unit. A portable CO2 fire extinguisher was used to extinguish the flame. The high current caused by the harmonic filter failure caused a short duration voltage dip on the main 11KV bus that caused all the thrusters to come off line and a brownout due to the online generators disconnecting from the bus. At 0659 hours the vessel reached the red watch circle and the emergency riser disconnect sequence was initiated. At 06:59:45 hours the separation of the LMRP was confirmed at a distance of 185 feet from location resulting in the release of synthetic base drilling fluid. A total mud loss of 547 bbls of which 383 bbls was oil base. No visible sheen was reported at the surface. While attempting to restore thruster control, the rig blacked out at 0702 hours approximately 290 ft from location. At 0705 hours, power was restored and at 0706 hours thrusters restored. Position was stabilized by 0717 hours approximately l456 ft from location. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | Y | Synthetic Oil Base Mud (SOBM) | Y | 16086 | N | N | N | N | N | Y | Synthetic Oil Base Mud (SOBM) | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-11-08 | 1400 | Helis Oil & Gas Company, L.L.C. | N |  |  |  | GOM | 2 | SS | 53 | G26051 | 13 | 15 | 1 | CAIS |  |  |  | The crew was working on leveling and squaring up the deck which had just been lowered over the bullet and resting on the ring plate. Below the ring plate was an installation aid scaffold with tarps installed. The superintendent began trimming grating on the deck with a torch resulting in the tarps catching fire. Fire extinguishers on the deck as well as a water hose from the L/B Superior Endeavor were used to extinguish the fire. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | Y | Construction | Y | N | N | N | N | N | N | N | N
2006-11-12 | 700 | Newfield Exploration Company | Y | N |  | 2007-01-31 | GOM | 5 | WC | 294 | G04090 | 44 | 30 | C | CAIS |  |  | 13162 | Operator stated they were preparing to shut-in the WC294 A structure for hot work and they went to Scada onboard 294A and remotely shut-in well C-2 on 294C prior to shutting in the SDV on WC294A host facility. Operator states they were unaware that the 294C2 well did not shut. Stated the PSH 1 and 2 failed. They also heard then observed a large amount of gas vapors escaping to the atmosphere from what they believed to be the PSV on the fuel gas system. Upon arrival at WC-294-C it was discovered that the departing pipeline had parted. The investigation revealed that fragments from the rupture of the pipeline riser damaged the pneumatic boat loop ESD, which shut-in the C-2 well. This ESD system is separate from that of the remote ESD system. | [6 empty] | N | N | Y | N | N | N | N | N | N | N | N | N |  | N |  | Y | pipeline and structural damage | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | Y | N | N |  | N | N | N | N | Y | N | N | N | N
2006-11-16 | 631 | Petrobras America Inc. | N |  |  |  | GOM | 3 | GB | 244 | G15860 | 2115 | 123 |  |  | T.O. F100 | SS |  | Motor oil that had accumulated over time on top of the #2 EMD caught fire causing minimal damage. The small fire was discovered by personnel in the immediate area, the fire was extinguished with a 30# handheld unit. The surface area on top of the engine was cleaned and the engine was ready to return to service when needed. No injuries to personnel or pollution occurred as a result of the incident. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-11-17 | 1020 | Pogo Producing Company | Y | N |  | 2006-02-16 | GOM | 1 | SP | 49 | G02177 | 450 | 9 | A | FIXED |  |  |  | Operator making rounds on the platform discovered a fire on the Glycol Surge Vessel BBC- 0200. He immediately alerted all crew members and shut in platform with the ESD system. Fire fighting procedures were followed; the fire was extinguished with in 10 minutes. The crew continued to spray the unit for cooling purposes and to prevent reignite. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | Y | N | N | N
2006-11-17 | 830 | Apache Corporation | N |  |  |  | GOM | 2 | SS | 193 | G13917 | 87 | 50 | A | FIXED |  |  |  | The low pressure compressor shut down and a small flash of flame emanated from the left bank air breather. A mechanic was attending the unit and a 30 lb. dry chemical unit was briefly discharged on the air breather. A faulty fuel gas regulator caused the fuel mixture to run rich causing the resultant flash. The fuel gas regulator was changed out immediately and the compressor put back in service without event. There was no damage to the compressor, no pollution, no injuries. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-11-18 | 1230 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | GC | 205 | G05911 | 2590 | 90 | A-Genesis Spar | SPAR |  |  |  | The contract crew was painting the liquid outlet of the test separator, line heater with high temperature paint. The painter turned to dip the brush in the paint can, turned back to apply paint on the piping and noticed a flash flame at the point where paint was previously brushed on. He extinguished the flame by covering it with a rag. According to the instructions on the paint container, red oxide 370, the temperature the paint was good for 175-275 degrees. The temperature on the piping was 262 degrees. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-11-18 | 1330 | Helis Oil & Gas Company, L.L.C. | N |  |  |  | GOM | 5 | VR | 68 | G25972 | 24 | 15 |  |  | ATWOOD RICHMOND | SU |  | Flash fires in mud room after well testing operations. Welder was told to cut 6" mixing line pipe in the number one pit room. During the initial cut and three attempts later, the line continued to catch fire and had to be put out with a fire extinguisher. Apparently condensate from well testing operations had entered mud pit system and caught fire while attempting to work on same. Approximately 4 ft flames ran out of end of pipe and up the wall in the pit room. Fluid and flames ran out of the pipe onto the floor igniting approximately 6 to 10 ft of area of fluid. This was extinguished with a fire extinguisher. The main issue here was that nobody in a supervisory position elected to stop this process after the first fire. The torch was used 3 more times to cut the pipe and the fire started again each time. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-11-20 | 645 | Devon Energy Corporation | N |  |  |  | GOM | 1 | MP | 259 | G07827 | 390 | 59 | A | FIXED |  |  |  | Flash Gas Compressor Shut-in due to PSH. A small flame was observed at the exhaust expansion joint. Flame was extinguished immediately with water. Compressor was left Shut-in for further observation. No Damage. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-11-20 | 1900 | Chevron U.S.A. Inc. | N |  |  |  | GOM | 2 | SS | 181 | G04231 | 67 | 33 | K | CAIS |  |  |  | The QCP crew was installing new flow lines on wells that were damaged by the 2005 storms. At the time of the incident, the welder was adding a thread-o-let on the flowline for a corrosion coupon. The piping was double blocked on each end, header side and wellhead end, and was gas free. The SCADA Technicians were simultaneously conducting calibrations on the SCADA chokes. The automated chokes are installed downstream of the wing valve, in the section of piping that had been monitored and had no indication of hydrocarbons. The technician stroked the automated choke on well K-1 and apparently trapped gas was released and caused a minor flash within the piping. There was no visible flame, only a burst of air released from the thread-o-let with enough force to blow the welders shirt. The SCADA Technicians were put on standby until the hot work was completed. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-11-20 | 1100 | El Paso Production Oil & Gas Company | N |  |  |  | GOM | 5 | VR | 356 | G17921 | 262 | 78 | A | FIXED |  |  |  | At 11:00 a.m. an Operator was walking around the compressor and noticed a fire on the compressor engine near the left turbo. He sounded the fire alarm, located a fire extinguisher and put out the fire. Also, he shutdown the compressor, set off the ESD system and winged in all wells. No injuries. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-11-23 | 1950 | Shell Oil Company | Y | N |  | 2006-01-31 | GOM | 2 | ST | 300 | G04240 | 300 | 77 | A | FIXED |  |  | 15208 | The diver was working on the Northwest corner of South Timbalier 300, Platform A at a depth of -30 feet. He was in the process of relocating an anode for the installation of pipeline risers for W&T Offshore (pipeline segments 15208 and 15209). When he struck an arc an explosion occured. An apparent build-up of oxygen occurred in a cavity of the anode. The explosion knocked the diver unconscious. The diver was being watched on live video and was immediately recovered to the surface after the explosion. His helmet was removed and he was placed on a backboard. He was treated by the onboard medic and was found to have facial lacerations, a chipped tooth, and sore ribs. The diver was stabilized and evacuated to Terrebonne General Medical Center at 2200 hours. He was held overnight for observation and released from the hospital at 1050 hours on November 26, 2006. The diver will be out of work for three weeks. He had a follow-up doctor's appointment scheduled for that week and he should be released to full duty. |  |  | 1 |  |  |  | Y | N | Y | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | Y | N | Y | Construction | Y | Y | N | N | N | N | N | N | N
2006-11-24 | 2245 | Shell Oil Company | N |  |  |  | GOM | 1 | MC | 807 | G07963 | 2933 | 67 | A-Mars TLP | TLP |  |  |  | Control room received smoke alarm from SW hull. Dispatched fast responders who confirmed smoke. Tripped platform ESD and mustered personnel to boats. Sent 2-man team with full bunker gear into hull. Observed small fire at composite cooling fan on 200 hp electric motor. Type of motor: Drill cooling/waterflood pump. Fire extinguished w/ 20# ABC extinguisher. Posted fire watch for 30 minutes. Resumed normal platform operations by 11:30 pm. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-11-29 | 2104 | Merit Energy Company | N |  |  |  | GOM | 5 | EC | 254 | G02039 | 164 | 74 | B | FIXED |  |  |  | Small fire on board the REM Commander. Smoke was noticed coming from under the cowling of the air compressor. The dive technician opened cowling and saw a flame around the alternator. The compressor was shut down and the fire was immediately extinguished. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | Y | N | N | N | N | Y | P&A operations conducted on toppled wells | Y | N | N | N | N | N | N | N | N
2006-11-30 | 1600 | Nexen Petroleum U.S.A. Inc. | N |  |  |  | GOM | 3 | EI | 295 | G02104 | 224 | 75 | A | FIXED |  |  |  | A fire occurred on compressor No. 1 exhaust system as a result of a bolt failure on the compressor lube oil pump. The failure allowed oil to spray onto the cooling fan which blew the oil onto the compressor's insulated exhaust. Oil penetrated the insulation and caught fire. Operator discovered the fire and quickly extinguished it using a handheld 30# unit. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-12-02 | 1700 | Eni Petroleum Co. Inc. | N |  |  |  | GOM | 1 | WD | 89 | G01088 | 220 | 23 | A | FIXED |  |  |  | Platform received call via satellite phone that phones were out. Operator went to the communications building (belonging to Stratos Communications) to check on power. Opened the door and found smoke in the building. Operator sounded the alarm. Cut power to the building. Mustered the fire team. Non fire team directed to the capsule. Found to be a small electrical fire. Used hand-held unit to extinguish the fire. Placed fire watch. Contacted shore base for notification of on-call Eni personnel. Stratos attended the incident the following morning and replaced a burned up battery charger. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-12-02 | 742 | Shell Oil Company | N |  |  |  | GOM | 1 | MC | 806 | G07962 | 3003 | 77 |  |  | T.O. DISCOVERER SPIRIT | DS |  | Fire was observed in clothes dryer by catering personnel. The employee closed to the phone contacted the D.P. control room and advised them there was a fire in the laundry room while the other employee got a fire extinguisher, turned off the dryer and opened the door and began extinguishing the fire. Due to the amount of smoke both employees were forced to evacuate the laundry room. The rig fire alarm system was activated and the primary fire team and the rig electricians were sent to the scene, and rig personnel were instructed to go to their muster stations. Ventilation was secured by the D.P. control room and the electricity was secured at breaker by electricians. The fire was reported out at 8:20 and all personnel were cleared from their muster stations. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | Y | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-12-03 | 2230 | Arena Offshore, LLC | N |  |  |  | GOM | 1 | WD | 87 | G27182 | 194 |  |  |  | HERCULES 252 | JU |  | Clothes dryer with bath towel in it was found smoldering due to vent dust not being cleaned out properly and the dryer was overloaded also. Employee that discovered the smoke made an announcement over the P.A. after using a fire extinguisher the fire team moved the towels and ventilation was set up to air out the smoke from living quarters. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | Y | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-12-04 | 2300 | W & T Offshore, Inc. | Y | N |  | 2007-10-02 | GOM | 1 | MP | 69 | 00372 | 48 | 11 | E | CAIS |  |  |  | At approximately 09:45 on 12/4/2006, there was a process upset on MP 69D platform. This closed the incoming boarding valve from MP 69 E. The E-1 well was the only well flowing into this line at the time. The operators tried to catch the boarding valve before the Echo platform shut in, but did not do it in time. At approximately 10:45 the operators on MP 69D heard a loud boom. They went outside the quarters and discovered that it had come from MP 69 Echo. They could smell the gas in the air. They called the field boat over to go over and start the investigation. On arrival at Echo they observed missing grating and damage to the riser. They thought that the 6" pipeline had burst. They radioed back their finding to the Lead Operator on MP 69D and he called the situation into his management. The decision was made to shut down the investigation that night due to weather. Pollution volume estimated at 25 to 30 gallons. | [6 empty] | N | N | Y | N | N | N | N | N | N | N | N | N |  | N |  | Y | Platform Damage | N | N | N | N |  | Y |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-12-04 | 1330 | PANACO, INC. | N |  |  |  | GOM | 4 | EB | 165 | G06280 | 863 | 90 | A | FIXED |  |  |  | While cutting rusty stud bolts off a flange, a piece of slag hit the deck and rolled to a deck drain. A flash fire occurred with a duration of approximately two seconds and was extinguished immediately, utilizing one hand-held fire extinguisher. There were no injuries or pollution. Precautionary measures had taken place prior to cutting the bolts. The drain was plugged and filled with water. The gas sniffer was used and the gas reading was zero on the gas detector, which was tested. The gas detector had been calibrated on 27-Nov-2006. A JSA had been conducted before the operation began, and a Hot Work Permit was in place. This is the initial and final report. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | Y | piece of slag from welding
2006-12-04 | 1530 | Dos Cuadras Offshore Resources, LLC | N |  |  |  | PAC | 8 | 6B | 5064 | P00234 | 290 | 8 | HABITAT |  |  |  |  | Welder was cutting grating near the south east corner of the switch gear room when he noticed the 1" gap where the the wall meets the grating was on fire. The fire was quickly extinguished and all combustable material was removed from the wall. The wall is made with spray foam to seal the crack between the wall and grating. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | N
2006-12-05 | 1800 | Apache Corporation | Y | N |  | 2007-03-01 | GOM | 3 | EI | 158 | G01220 | 80 | 40 | C | FIXED |  |  |  | 'Two contract employees with United Production and Construction Services (UPCS) sustained flash fire injuries on December 5,2006 as a result of a flash fire that occurred inside a skim tank as the tank was undergoing major renovations. The UPCS Supervisor, sustained a small flash burn to his neck but did not seek medical attention. Another worker who was nearest to the entrance of the manway of the skim tank sustained second degree burns to both hands and a flash burn to his face, neck and ears. |  |  | 1 |  |  |  | Y | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | Y | N | N | N | Y | N | N | N
2006-12-05 | 1650 | ExxonMobil Oil Corporation | N |  |  |  | GOM | 1 | SP | 93 | G01619 | 446 | 18 | A | FIXED |  |  |  | During hot work operations involving cutting steel near the compressor building on the top drill deck, a piece of slag fell to the deck below from the drill deck outer perimeter and landed on a cotton towel which was being used to protect electrical cables connecting a temporary generator to the platform MCC room. The towel provided a cushion padding protecting the cables as it entered the MCC building. Operators working in the MMC area noticed the towel smoldering right away and used one short burst from a fire extinguisher and also poured water on the towel. There were no visible flames observed on the towel. The electrical cables and towel have been moved. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-12-09 | 615 | Mariner Energy, Inc. | N |  |  |  | GOM | 3 | EI | 212 | G05503 | 86 | 66 | A | FIXED |  |  |  | While on first rounds of the day, operator noticed fire approx. 3 ft. up on still column of glyco reboiler. Operator and clerk extinguised fire with (2) 30# hand held fire extinguishers. Shut-in glycol unit, spraying with fresh water hose. No injuries, no major damage. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | Y | N | N | N
2006-12-10 | 1830 | Nexen Petroleum Offshore U.S.A. Inc. | N |  |  |  | GOM | 5 | VR | 340 | G02091 | 223 | 100 | A | FIXED |  |  |  | Welding operations were being performed at the time of the fire. Welders were on the inside of the wet oil tank welding. A bag of filter media that was left lying against or near the outside of the tank was ignited by the welding operations. The fire watch immediately extinguished the small fire. No damage to the platform or injuries to personnel on the platform. Platform has been shut-in since the Hurricane Rita due to the storm damge. It is in the process of being repaired. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N | N
2006-12-12 | 740 | Paloma Offshore, LLC | Y | N |  | 2006-02-28 | GOM | 4 | MI | 656 | G03096 | 75 | 12 | 3 | CAIS | PRIDE MISSISSIPPI | JU |  | The driller noticed the fire and notified the tool pusher. The alarm was sounded. The The maintenence crew shut down electrical power while the assistant driller and a floor hand extinguished the fire with two thirty pound ABC class extinguishers. A fire hose was also used to the cool the equipment. There were no injuries or pollution. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | Y | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-12-13 | 1750 | Newfield Exploration Company | Y | N |  | 2007-03-01 | GOM | 3 | SM | 49 | 00787 | 85 | 40 | A | FIXED |  |  |  | 'A glycol fire occurred on the SM Block 49, A platform glycol reboiler, adjacent platform decking and crane gantry at approximately 17:45 hours on December 13, 2006. Hot Glycol was initially observed to be percolating uncontrolled out of the glycol reboiler still column vent by an Island Operating employee. Upon observing the malfunctioning glycol reboiler, he immediately alerted the platform operator person in charge (PIC), and actions to shut down the glycol reboiler were initiated immediately. The hot glycol percolating from the still column vent was being blown onto portions of the adjacent glycol reboiler burner base and exhaust stack. Ignition of the hot glycol occurred immediately upon coming in contact with exposed portions of the burner base and exhaust stack. Once the hot glycol became ignited, the immediate area surrounding the glycol reboiler had to be evacuated of all personnel. The resulting fire continued for approximately fifteen (15) minutes before being controlled and extinguished by the onboard personnel with fourteen (14) hand held portable and two (2) wheeled chemical fire fighting units. There were no injuries and no pollution reported as a result of this incident. The glycol reboiler still column and vent and burner exhaust stack are parallel and positioned within approximately two (2) feet of each other. The burner exhaust stack is insulated from the burner base to within approximately three (3) feet of the top of the burner exhaust stack arrestor (SA). Once the hot glycol was initially ignited, hot glycol continuing to percolate from the still column vent continued to be ignited and burned as it came in contact with the adjacent platform decking and crane gantry. The platform living quarters located approximately twenty (20) from the glycol reboiler unit and on the same deck level sustained no damage. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | N
2006-12-14 | 1500 | Nippon Oil Exploration Offshore U.S., Ltd. | N |  |  |  | GOM | 3 | SM | 243 | G04270 | 23 | 15 | C | FIXED |  |  |  | Flash fire in generator room in electrical panel. Fire put out with CO2 extinguisher. Platform on production with second generator running. No injuries. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-12-15 | 400 | PetroQuest Energy, L.L.C. | N |  |  |  | GOM | 2 | SS | 72 | 00060 | 30 | 7 | J | FIXED |  |  |  | Small fire occurred when glycol reboiler caught on fire. The fire was put out with a water hose on the facility. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N | N
2006-12-20 | 2200 | Williams Oil Gathering, L.L.C. | N |  |  |  | GOM | 4 | GA | A244 | G22219 | 363 | 68 | A | FIXED |  |  |  | A small electrical fire occurred on the air conditioning unit for the motor control center building on GA-A-244 platform. No injuries were sustained during the incident. The unit was locked and tagged out of service. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | N | N | N | N | N | Y | N | N |  | Y | N | N | N | N | N | N | N | N
2006-12-22 | 115 | Exxon Mobil Corporation | N |  |  |  | GOM | 2 | GC | 18 | G04940 | 750 | 96 | A | FIXED |  |  |  | A small fire occurred on the platform. The fire was in a cargo basket, lined with a trash compactor bag, containing cardboard, paper, used plastic gloves, and rags. The fire was immediately extinguished using a hand held extinguisher and water hose. No injuries, damage, or loss of equipment. No cause was ever determined. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | N
2006-12-22 | 200 | PANACO, INC. | N |  |  |  | GOM | 4 | EB | 165 | G06280 | 680 | 105 | A | FIXED |  |  |  | An employee of Gulf Coast Measurement went outside of building and noticed flame escaping from the muffler of the Universal compressor. He immediately notified the Panaco night operator and then woke the Panaco Foreman. The Panaco night operator immediately shut-down the compressor, thus extinguishing the visible flame. Further investigation revealed a hole in underside of muffler allowing flame to escape. Fire blanket was stripped back and compressor was observed for approximately two hours without any further flame. No fire fighting equipment was used during this incident. East Breaks 165 is currently shut-in. Universal compression is working to get replacement parts and personnel mobilized, notifications will be sent when coming back on line. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N |  | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | N | N | N | N | N | N
2006-12-31 | 1930 | Apache Corporation | N |  |  |  | GOM | 1 | WD | 41 | G01073 | 83 | 15 | B | FIXED |  |  |  | Lightning struck Apache's unmanned WD 41B facility causing a fire. Personnel on WD 41A saw the fire and went to 41B to extinguish it. By the time the operator's reached the facility the fire extinguished on its own due to the heavy rain. Due to safety precautions, no one was allowed to go on the facility until the next morning. It was discovered that the TSE on the generator performed properly shutting the platform down. The only damage was to the generator package. | [6 empty] | N | Y | N | N | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | Y | Lightning strike | N |  | N | N | N | N | N | N |  | Y | N | N | N | N | N | N | N |  | N | N | N | Y | N | N | N | N | N
TOTALS |  |  | 24 | 0 | [15 empty] | 0 | 1 | 2 | 0 | 0 | 3 | 3 | 134 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 2 |  | 0 | 3 | 1 | 4 |  | 2 | 16086 | 0 | 0 | 0 | 0 | 0 | 1 |  | 104 | 17 | 5 | 2 | 0 | 5 | 0 | 15 |  | 74 | 53 | 0 | 5 | 2 | 5 | 0 | 0 | 11